Suggested Specification for:

RIELLO RS /E-EV

Operation: Full Modulation Single of Dual Fuel Gas (Natural or LPG)

Table of Contents

A.  General Requirements	1

B.  Burner Description	2

C.  Burner Construction	2

D.  Fuel / Air Ratio Control	3

E.  Ignition System	3

F.  Burner Mounted Controls	3

H.  Main Gas Train	3

I. Modulating Burner/Boiler Control	4

## A.  General Requirements

Furnish and install ______ (UL) (ULC) (ETL) listed Gas fired burner(s). Burner construction, design, components and installation shall adhere to all applicable code requirements.

Omit the following retro-fit boiler requirements if project calls for new boiler / burner package(s)

Replacement burner shall be installed in (Watertube), (Scotch Marine), (Firebox), (Cast Iron), (Other) _____________________ type boiler(s). The boiler model is _______________ as manufactured by ______________________.

Burner manufacturer’s recommendations for combustion chamber requirements shall be followed. The existing combustion chamber shall be modified and new material supplied as required.

Each boiler shall be equipped with a complete factory packaged combustion and fuel supply system, with integrally mounted fuel/air ratio controls for single-location accessibility.

Basis of design (burner): Riello Model RS____.

All components on burner shall have a minimum 24 month warranty from day of start-up

## B.  Burner Description

Provide a forced draft flame retention type automatic burner.  The burner(s) shall be designed to fire _____________ kW of (Natural Gas) (and/or) (Propane) with a supply pressure of _____ kPa.

Burner operation will be full modulation (on gas)(on both fuels). Burner shall operate with minimal vibration and noise at the specified rate. The burner must operate with 15% – 20% excess air and CO must be less than 15 ppm in the products of combustion.

## C.  Burner Construction

Burner housing shall be die cast aluminum “monobloc” type construction. The burner mounting flange must support the burner weight on the boiler independent of any support.

Burner shall be furnished with a stainless-steel flame retention type of combustion head, capable of withstanding temperatures up to 1400oF. This combustion head shall incorporate a diffuser and sleeve that is to direct excess air either around the flame or directly through the diffuser vanes. Adjustment to the diffuser insertion shall be made external to the burner and can be made while burner is in full operation.

Burner shall be equipped with (service slide bars [R_28 – 190 size]) (hinged construction [R_280-800 size]) that allow for full access to the burner drawer assembly without removing the burner chassis from the boiler.

Burner shall have a flame inspection window positioned at the rear center of the burner housing.  Flame shall be viewed without removing any covers.

Burner shall come complete with a high efficiency, totally enclosed fan cooled motor (TEFC) _____volt, ___ phase, ___Hz, and a dynamically balanced reversed incline blower wheel.

The sound rating of the burner shall not exceed 85 dBa when measured at 3 feet from the burner.

A protection screen shall be installed on the air intake housing.

Burner shall utilize a balance aluminum reverse incline fan wheel directly mounted to the motor shaft.

## D.  Flame Safeguard & Fuel / Air Ratio Control

Electronic Linkageless Burner Management System: Siemens (LMV36, RWF55 & AZL Service Display) (LMV37, RWF55 & AZL Service Display) (LMV51 & AZL Service Display) (LMV52 & AZL Service Display) shall provide the flame safeguard control and firing rate modulation capabilities.

LMV36 – Dual Fuel application, VFD optional

LMV37 – Single Fuel application, VFD optional

LMV51 – Single/Dual fuel application

LMV52 – Single/Dual fuel application with option for VFD.

Include: Variable Speed Drive on combustion air fan

## E.  Ignition System

The burner gas ignition system shall utilize natural or propane gas as the fuel source. The gas pilot system shall include spark ignited pilot assembly, 8000 Volt ignition transformer, pilot safety shut off valve, pilot gas pressure regulator and manual gas shutoff cock.

## F.  Burner Mounted Controls

Burner shall be equipped with an integral burner mounted control panel consisting of necessary motor starters, overloads, lights and switches. Burner shall be supplied with an integral AUTO/MANUAL/OFF switch that incorporates a control toggle that will allow a technician to manually drive the burner servomotor from low fire to high fire or high fire to

low fire and the means to stop at any position in between, in a smooth and controlled method.

The burner shall be equipped with an SPDT air pressure switch that will not allow burner to start if there is insufficient combustion air, which is checked prior to each ignition attempt. Before the burner can start the airflow switch must be in the open position to prove the switch is not giving a false signal of sufficient combustion air pressure.

BMS Communication: (MODBUS) (BacNet), include gateway as required with points list.

HMI Interface (and 2 boiler lead-lag sequencing system)

Burner mounted, high definition 4.3” color HMI capacitance multi-function touch-screen and controller. Providing burner function access boiler operators with clean visual navigation.

BMS communication via Modbus RTU (serial) or Modbus TCP (Ethernet) also BACnet IP or MSTP, Lonworks, Metasys – with Gateway. Points-list available (protocol dependent).

Visual display of burner firing rate and boiler temperature (or pressure), and setpoint.

Time stamped history of the last 20 error codes received from the combustion controller (Siemens LMV3 or LMV5)

English text description for each error diagnostic code

Real-time burner operating information visually available:

Fuel ON

Fan ON

Call for Heat

Fuel servo position

Flame signal

Boiler Safeties (OK/Alarm)

Air switch (OK/Alarm)

Low Gas Pressure (OK/Alarm)

High Limit or High Gas Pressure (Ok/Alarm)

Water Level (OK/Alarm)

Error Code

Total run hours

Total burner starts

Operating Controls and User Inputs

Automatic/Manual/Remote Modulation

Local Setpoint

Hot Stand-By (extra sensor required for steam systems)

Outdoor Air Temperature Reset Parameters

Pump / Isolation Valve Signal (Dry-Contact or BMS)

Pump / Isolation Valve: Adjustable Time Delay

Lead-Lag Control for Two Burner/Boiler System (Must Have Matching Touch-Screens) [ONLY APPLICABLE IN TWO BURNER SYSTEM]

Ethernet cat 5/6 cable connection between the two burners

Start-Lag: Minutes: Firing rate of first burner to trigger start of the second burner

Stop-Lag: Minutes: Firing rate of first burner to stop second burner

Start-Delay: Minutes: Delayed second burner start after start-lag is triggered

Stop-Delay: Minutes: Delayed second burner stop after stop-lag is triggered

Boiler Maximum Setpoint

Boiler Minimum Setpoint

Lead Rotation Interval: Hours: Local or Remote Interval Time)

## H.  Main Gas Train

1. U.L. Requirements

The gas valve train shall contain the following:

- Manual Shutoff cock

- Main gas pressure regulator (Engineer - Specify “tight shutoff type” when gas supply

pressure exceeds 1 PSIG).

- Two automatically operated safety shut-off valves  (Specify one with valve seal over-travel and proof of closure switch when capacity is over 5.0 MBH)

- Manual reset low and high gas pressure switches (specify as standard above 2500

MBH - optional at 2500 MBH and below).

- Manual leak test cock.

- Burner manifold gas pressure gauge (optional)

- FM Requirements

(For units requiring FM compliance, in addition to U.L. requirements, add the following to the UL scope)

- U.L. listed leak test cock.

- One of the two automatically operated safety shut off valves must include valve seal over travel and proof of closure.  Both valves shall carry an FM label.

- Both automatically operated motorized gas valves shall be equipped with 13 second timing motorized operators.

- IRI Requirements

(For units requiring IRI compliance, add the following to the UL scope)

a. U.L. listed leak test cock.

b. Both automatically operated safety shut off valves (main and auxiliary) shall have motorized operators, one with valve seal over travel and proof of closure.

c. One normally open vent valve sized according to IRI requirements.

d. Manual reset low and high gas pressure switches (specify for all burner capacities).