RS/E LN

Linkage-less Low NOx Power Burner

| Project | Project Name | Click here to enter text. | UL295/ UL 296 The RS/E LN series has been designed for use in low or medium temperature hot water boilers, steam boilers, diathermic oil boilers, warm air appliance, and similar applications. Operation can be “two stage progressive” or, alternatively, “modulating” with the installation of a PID logic regulator and respective probes. RS/E LN series burners guarantee low NOx emissions, high efficiency, reducing fuel and running costs while the exclusive design provides simple use and maintenance with low sound emissions. |
| --- | --- | --- | --- |
|  | Site Location |  |  |
|  | Installation Altitude |  |  |
|  | Engineering Firm |  |  |
|  | Installing Contractor |  |  |
|  | Riello Representative |  |  |
|  | Rep. Contact Information |  |  |
|  | RBNA Project Number |  |  |
|  | Job Name |  |  |
|  | Equipment Manufacturer |  |  |
|  | Equipment Model |  |  |
|  | Equipment Type |  |  |
|  | Input |  |  |
|  | Fuel Type |  |  |
|  | Chamber Length |  |  |
|  | Chamber Width |  |  |
|  | Chamber Height / Diameter |  |  |
|  | Chamber Pressure |  |  |

Project Notes:

| General Burner Data | RS 45 LN | 120V/1Ph/60Hz |  |
| --- | --- | --- | --- |
|  | RS 68 LN | 208-230V/3Ph/60Hz |  |
|  |  | 460V/3Ph/60Hz |  |
|  |  | 575V/3Ph/60Hz |  |
|  | RS 120 LN | 208-230V/3Ph/60Hz |  |
|  |  | 460V/3Ph/60Hz |  |
|  |  | 575V/3Ph/60Hz |  |
|  | RS 160 LN | 208-230V/3Ph/60Hz |  |
|  |  | 460V/3Ph/60Hz |  |
|  |  | 575V/3Ph/60Hz |  |

| Optional Accessories | RWF 55 PID Modulating Control | X |
| --- | --- | --- |
|  | Air Intake Adaptor |  |
|  | Propane Conversion Kit |  |
|  | Alarm Horn with Silence Switch | X |
|  | Local/ Remote control Switch | X |
|  | Additional Indicating Light |  |
|  | 3 Dry Contact Relays | X |
|  | Combustion Head Extension |  |
|  | Pre-Wire and Assembled Gas Train |  |
|  | UV Scanner | X |
|  | Temperature Sensor |  |
|  | Pressure Sensor |  |
|  | 4.3” HMI |  |
|  | Control Circuit Transformer |  |

Standard Feature

- Siemens LMV37 microprocessor flame safeguard

- UV scanner flame detection

- Premium efficiency motor

- Aluminum combustion air fan

- Die cast aluminum mono-bloc construction

- Air suction circuit lined with sound-proofing material

- Fan with reverse curve blades

- Fully independent air and fuel actuators featuring air damper for air setting and butterfly valve for regulating fuel

- Combustion head that can be set based on the required output

- High gas pressure switch to stop the burner in the case of excess pressure on the fuel supply line

- Low air pressure switch stops the burner in case of insufficient air quantity at the combustion head

- Post-ventilation through parameter setting

- Burner on/off switch

- Flame inspection window

- Manual or automatic output increase/decrease switch

- Slide bars for easier installation and maintenance

- NEMA 1 electric protection level. - Single point 3 ph power connection with optional Control Circuit Transformer Installed

- 5 indicator lights, Power ON, Main Fuel ON, Call for Heat, Ignition, Flame failure.

- 1 three-way switch: off/local/remote

- 1 Alarm Horn

- 1 Alarm silence push-button

- 3 dry contact relays

Output Capacity Chart

Max. firing rates are based on zero furnace backpressure, ambient temperature of 68 °F, barometric pressure 394 inches WC, 329 ft. elevation a.s.l. For more details and final burner selection refer to applicable installation manual.

Burner Data Chart

|  |  |  | RS 45/E LN | RS 68/E-EV LN |  | RS 120/E-EV LN | RS 160/E-EV LN |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | General Data |  |  |  |  |
| Burner operation |  |  | Progressive 2 stage or low-high-low / full modulation with supply of modulating signal |  |  |  |  |
| Servomotor | Make & Model |  | Siemens SQM33 |  |  |  |  |
| Fire Input Range (min / max) |  | MBtu/Hr | 341 - 2037 | 570 - 3258 | 1136 - 4924 |  | 1136 – 7046 (6302*) |
| Working temperature range | min / max | OC | 0-40 |  |  |  |  |
|  |  | OF | 32-104 |  |  |  |  |
| Combustion air fan type |  |  | Centrifugal with reverse incline blades |  |  |  |  |
| Combustion air temperature | max. | OC | 60 |  |  |  |  |
|  |  | OF | 140 |  |  |  |  |
| Approvals |  |  | cULus (UL795, CSA 3.4) CSD-1 Compliant |  |  |  |  |
|  |  |  | Fuel Data |  |  |  |  |
| Fuel heating value | Natural gas | Btu/ft3 | 1000 |  |  |  |  |
| Specific gravity | Natural gas |  | 0.64 |  |  |  |  |
|  |  |  | Electrical Data |  |  |  |  |
| Main voltage | volts / phase / hertz |  | 120/1/60 | 230-460-575/3/60 |  |  |  |
| Control voltage | volts / phase / hertz |  | 120/1/60 (separate control voltage supply required on 3 phase integral flame safeguard units) |  |  |  |  |
| Fan motor size | HP |  | 0.5 | 3.0 | 3.0 |  | 7.5 |
| Amperage draw | Motor | Amps | 5.2 | 7.8 – 3.9 – 3.1 | 7.8 – 3.9 – 3.1 |  | 17.8 – 8.9 - 7.1 |
| FLA |  |  | 11.5 | 13.1-6.4-5.2 | 13.1-6.4-5.2 |  | 23.0-11.3-9.1 |
| MCA |  |  | 13.0 | 16.0-8.0-6.0 | 16.0-8.0-6.0 |  | 29.0-14.0-11.0 |
| MOCP |  |  | 15.0 | 20.0-10.0-10.0 | 20.0-10.0-10.0 |  | 45.0-20.0-15.0 |
| Motor type |  |  | TEFC |  |  |  |  |
| Ignition transformer(s) |  | GAS | 120V-1.6A / 1x7kV-23mA | 120V-1.6A / 1x8kV-20mA |  |  |  |
| Flame safeguard | Riello | Model | Siemens LMV37 |  |  |  |  |
| Burner protection level |  | NEMA | 1 |  |  |  |  |
| Operation |  |  | Intermittent (1 stop minimum every 24hr of continuous operation) |  |  |  |  |
|  |  |  | Emissions |  |  |  |  |
| Sound level |  | dBa | 72 | 75 | 77 |  | 83.1 |
| CO2 operating range |  | % | 9 – 10.5% |  |  |  |  |
| CO emission (@ 3.0% O2) |  | ppm | <25 |  |  |  |  |
| NOx emission (@ 3.0% O2) |  | ppm | <40 |  |  |  |  |
| All emission values are based on laboratory conditions and are for reference only. Emissions testing conducted on European DIN combustion test chambers. |  |  |  |  |  |  |  |
| Maximum input ratings based on furnace pressure of 0"w.c. Contact factory if required input is outside of that shown in operating charts located in the burner manuals. |  |  |  |  |  |  |  |
| Reference conditions: Ambient temperature 68OF (20OC). Barometric pressure 394"w.c. Altitude <2000 fasl. Contact factory for higher altitude selection. |  |  |  |  |  |  |  |
| *Firing rate for C - UL Canadian Listing (CNL) |  |  |  |  |  |  |  |

General Dimensions & Weight

| Burner Dimensions |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | A | B | C | D | E | F-F1 | G* | H |
| RS 45/E LN | 26" | - | - | 20-1/4" | 26-3/4" | 9" | - | 6-5/16” |
| RS 68/E-EV LN | 33-1/2” | 16-3/4" | 16-3/4" | 25-1/4” | 40-3/4" | 9-15/16” | 7-1/2" | 7-1/2" |
| RS 120/E-EV LN | 33-1/2” | 16-3/4" | 16-3/4" | 25-1/4” | 40-3/4" | 9-15/16” | 7-1/2" | 7-1/2" |
| RS 160/E-EV LN | 33-7/8” | 16-3/4" | 16-3/4" | 25-19/32” | 40-3/4" | 14-11/16” | 10-29/32" | 8-3/4" |
|  | I | L | M | N | O | V | P | Q |
| RS 45/E LN | 14-3/16" | 6-1/2" | 1-1/2” | 4-1/4" | 37-1/4" | 6-5/8" | - | - |
| RS 68/E-EV LN | 16-3/4” | 9" | 2" | 5-7/8" | 52-13/16” | 8-3/4" | 11-1/4” | 10-41/64” |
| RS 120/E-EV LN | 16-3/4” | 8-13/16" | 2" | 5-11/16" | 52-13/16” | 8-3/4" | 12-13/16" | 10-41/64” |
| RS 160/E-EV LN | 17-3/16” | 8-3/4" | 2" | 5-13/16" | 63-1/4” | 8-3/4" | 18-1/8" | 12” |

G* Maximum depth of the boiler door including the depth of the burner head thermal gasket.

RS 68-120-160/E-EV LN

RS 45/E LN

| Mounting Plate Details |  |  |  |
| --- | --- | --- | --- |
| Model | A | B | C |
| RS 45/E LN | 6-5/16" | 8-13/16" | 3/8”W |
| RS 68/E-EV LN | 9-1/6" | 12-13/16” – 14-1/2" | 5/8”W |
| RS 120/E-EV LN | 9-1/6" | 12-13/16” – 14-1/2" | 5/8”W |
| RS 160/E-EV LN | 9-1/6" | 12-13/16” – 14-1/2" | 5/8”W |

| Package Size |  |  |  |  |
| --- | --- | --- | --- | --- |
| Model | Dimensions - inches |  |  | Weight |
|  | A | B | C | lbs |
| RS 45/E LN | 47-1/4" | 23-5/8" | 28" | 152 |
| RS 68/E-EV LN | 59-1/16" | 33-1/2" | 39-3/8" | 201 |
| RS 120/E-EV LN | 59-1/16" | 33-1/2" | 39-3/8" | 201 |
| RS 160/E-EV LN | 59-1/16" | 33-1/2" | 39-3/8" | 275 |

Flame Safeguard

| Model |  | LMV37 |
| --- | --- | --- |
| Electrical Supply | V/Ph/Hz | 120/3/50-60 |
| Primary fuse | A | 6 |
| Ambient Conditions | %RH | 95 (no condensation) |
|  | °F | -4-140 |
| Flame Detection | Type | UV |
| Approval |  | cURus |

The Siemens LMV37 flame safeguard control is a microprocessor based parallel positioning system

Gas Train

CSD-1 and UL compliance Gas Train			SEE PROJECT FILE FOR FULL GASTRAIN DRAWING.

*USA installation excluding Massachusetts

OR

RIELLO NORTH AMERICA

Corporate Headquarters

2165 Meadowpine Blvd

Mississauga, ON L5N 6H6, Canada

USA OFFICE

35 Pond Park Rd.

Hingham, MA02043, USA

Phone: 905-542-0303

Fax: 905-542-1525